## Checklist
JA ESS Pre-Installation Checklist
Project Information: Please provide key information on the installation
Project Name |  |  |  | Project Address
Customer Type |  | Customer Name |  | Commissioning Contact (incl. Contact Details)
Contract Scope |  |  | Required Commissioning Start Date |  | Required Completion Date
Extended Warranty Agreement Signed | YES | NO | Commissioning Service (Chargeable / Free Issue) | NA | LTSA (Long-Term Service Agreement) Signed | YES | NA
Other Special Requirements / Notes:
Project Scenario：Please select the required functions and provide corresponding details accordingly
Number of Grid Connection Points |  |  | Number of battery cabinets |  |  | Parallel units in operation | YES NO
Peak Shaving & Load Shifting | (Charging/discharging schedule and electricity tariff are required; can be provided as an attachment or confirmed on site with the customer)
PV-ESS (PV-Storage Integration) | (Required: PV inverter brand, installed PV capacity, communication method; EMS1000 hardware required on site)
| PV Inverter Brand |  |  |  | Number of PV Inverters
| Installed PV Capacity (kW) |  |  |  | EMS1000 On Site (to be completed by presles rep) |  | YES NO
| Communication Method (Parallel / Data Logger) |  | Parallel Data Logger |  | Communication Protocol Integrated with Jianjie |  | YES NO
Black Start | (Confirm PV capacity, load demand, switching time, dry contacts; EMS1000 required)
| Installed PV Capacity (kW) |  |  |  | Total Load Power (kW)
| Presence of Inrush Loads |  | YES NO |  | Switching Time Requirement
| ACB Dry Contact Available |  | YES NO |  | EMS1000 On Site (to be completed by presles rep) |  | YES NO
Off-Grid System | (Confirm PV capacity, load demand, backup power availability; EMS1000 required)
| Installed PV Capacity (kW) |  |  |  | Number of PV Inverters
| PV Inverter Brand |  |  |  | Communication Method (Parallel / Data Logger) |  | Parallel Data Logger
| Total Load Power (kW) |  |  |  | Presence of Inrush Loads |  | YES NO
| Backup Power Available (Grid / Generator) |  | YES NO |  | EMS1000 On Site (to be completed by presles rep) |  | YES NO
Other: | (Application scenario and required functions shall be clearly defined)
Protection Functions：Please select the required function and provide corresponding details accordingly
Anti-Backflow / Export Limitation | (Meter type and installation location must be defined: LV or HV busbar; pre-wiring or on-site guidance required)
| Meter Model |  | Meter Installation Location |  |  | CT Ratio (Current Transformer Ratio)
Demand Control | (Meter type and installation location must be defined; maximum demand at grid connection point must be configured)
| Maximum Demand at Grid Connection Point |  |  |  | Shared Meter with Export Limitation Function |  | YES NO
| Meter Model |  | Meter Installation Location |  |  | CT Ratio
Capacity Protection | (Transformer capacity must be specified)
| Transformer Capacity |  |  |  | Maximum Loading Ratio (Default: 90%)
Power Limitation Mode | (Distribution cabinet configuration and main breaker specifications must be defined; recommended rating per cabinet: 315A)
| Power-Limited Operation |  | YES NO |  | Breaker Rating per Unit (A)
| Main Circuit Breaker Rating (A) |  |  |  | Power Limit per Cabinet (kW)
Topology Diagram | (Can be provided as an attachment)
|  |  | Confirmed By： |  | Date：

## Field Guidance
Checklist Field | Applicability / Priority | What We Need From Customer | Example | Why It Is Needed | Customer Note
Project Name | Mandatory - Every Project | Official project name used in contract / offer | Romania BESS Phase 1 | Reference for commissioning records | Must be completed.
Project Address | Mandatory - Every Project | Exact site location where commissioning will take place | Street, City, Country | Planning, travel, and site access coordination | Must be completed.
Customer Name | Mandatory - Every Project | EPC / owner / integrator company name | ABC Energy | Commercial and service reference | Must be completed.
Commissioning Contact | Mandatory - Every Project | Main site contact: name, phone, email | John Doe, +40..., email | Commissioning team needs one responsible site contact | Must be completed before service scheduling.
Contract Scope | Mandatory - Every Project | Confirm whether scope is equipment commissioning only or full installation + commissioning | Equipment Installation & Commissioning | Defines responsibility split between customer/EPC and JA | Must be completed.
Required Commissioning Start Date | Mandatory - Every Project | Requested start date for commissioning | 01/08/2026 | After-sales team planning | Date should be realistic and aligned with site readiness.
Required Completion Date | Optional | Target completion date if customer has a deadline | 05/08/2026 | Helps planning but may depend on site readiness | Provide if available.
Number of Grid Connection Points | Mandatory - Every Project | Number of PCC / grid connection points | 1 PCC / 2 PCC | Meter and protection strategy depend on this | Must be completed.
Delivery Quantity | Mandatory - Every Project | Number of delivered BESS cabinets / PCS / DC blocks | 20 cabinets | Used for configuration and commissioning planning | Must be completed.
Parallel Operation of Multiple Units | Mandatory - Every Project | Confirm whether multiple BESS units operate as one coordinated system | Yes if more than one unit operates together | Determines EMS1000 / communication setup | Must be completed.
Peak Shaving & Load Shifting | Standard Function - Complete if selected | Charging/discharging schedule, electricity tariff periods, expected control logic | Charge 00:00-06:00, discharge 17:00-21:00 | Used for EMS scheduling | Complete only if this function is required.
PV-ESS Coordination | Optional - Complete only if PV integration is required | Confirm PV inverter brand, PV capacity, inverter quantity, and communication method | Huawei, 2 MWp, 10 inverters, Modbus TCP | Needed for PV+BESS self-consumption or export control | Skip if no PV integration.
PV Inverter Brand | Optional - PV only | Exact PV inverter brand and model | Huawei SUN2000-100KTL | Checks communication compatibility | Required only if PV-ESS coordination is selected.
Installed PV Capacity | Optional - PV only | Total installed PV capacity in kW/kWp | 2000 kWp | Used for energy strategy and limits | Required only if PV-ESS coordination is selected.
Number of PV Inverters | Optional - PV only | Quantity of PV inverters and rating | 10 x 200 kW | Needed for communication mapping | Required only if PV-ESS coordination is selected.
Communication Method (Parallel / Data Logger) | Optional - PV only | How PV inverter data will be provided to EMS | Direct Modbus TCP / Data Logger | Defines integration route | Required only if PV-ESS coordination is selected.
Black Start | Advanced Optional - Latest Version / Special Project Only | Confirm if system must restart and energize loads without grid supply | Yes - black start required | Needs special design, EMS1000, load study, and backup logic | Not applicable for standard current grid-connected projects. Complete only if explicitly required and confirmed by JA.
Installed PV Capacity for Black Start | Advanced Optional - Latest Version / Special Project Only | PV capacity available for black-start/microgrid mode | 500 kWp | Needed only for backup/microgrid design | Skip for standard peak-shaving projects.
Total Load Power | Advanced Optional - Latest Version / Special Project Only | Critical load power expected during backup/black-start operation | 300 kW critical load | Determines whether system can supply the load | Skip unless black start/off-grid is selected.
Presence of Inrush Loads | Advanced Optional - Latest Version / Special Project Only | Confirm if motors, pumps, compressors, transformers, or high starting-current loads exist | Yes - 90 kW pump motor | High inrush can affect PCS/STS sizing and stability | Skip unless black start/off-grid is selected.
Switching Time Requirement | Advanced Optional - Latest Version / Special Project Only | Required transfer time during grid outage | <20 ms / <1 s / no strict requirement | Determines STS and backup suitability | Skip unless backup/off-grid function is selected.
ACB Dry Contact Available | Advanced Optional - Latest Version / Special Project Only | Whether breaker dry contact is available for status/control | Yes / No | Needed for automatic switching logic | Skip unless black start/off-grid is selected.
Off-Grid System | Advanced Optional - Latest Version / Special Project Only | Confirm if BESS must operate islanded without utility grid | Yes - off-grid operation required | Requires microgrid design, load study, and EMS1000 | Not applicable for standard current grid-connected projects. Complete only if explicitly required and confirmed by JA.
Backup Power Available (Grid / Generator) | Advanced Optional - Latest Version / Special Project Only | Confirm if generator or backup source is available | 500 kVA diesel generator | Used for microgrid backup control | Skip unless off-grid/backup function is selected.
Other Application Scenario | Optional | Clearly describe any other special function | SCADA, PPC, FCR, custom EMS | Allows JA to assess scope in advance | Complete only if there are special requirements.
Anti-Backflow / Export Limitation | Optional - Complete only if selected | Confirm if the system must prevent export to the grid | Zero export required | Requires meter at correct PCC and control configuration | Skip if export limitation is not required.
Meter Model | Conditional - Required for meter-based functions | Exact smart meter model and brand | Acrel DTSD1352 | Communication setup and compatibility | Required for export limitation, demand control, or self-consumption control.
Meter Installation Location | Conditional - Required for meter-based functions | Exact electrical location of meter | LV main incomer / MV side / PCC | Control accuracy depends on correct meter position | Required for export limitation and demand control.
CT Ratio | Conditional - Required for meter-based functions | Current transformer ratio | 1000/5A | Accurate power measurement | Required if CT-operated meter is used.
Demand Control | Optional - Complete only if selected | Maximum import/demand limit at grid connection point | 500 kW | EMS controls battery to avoid exceeding demand | Skip if demand control is not required.
Shared Meter with Export Limitation | Conditional | Confirm if export limitation and demand control use same meter | Yes / No | Avoids duplicate or incorrect meter configuration | Complete only if both functions are selected.
Capacity Protection | Optional - Complete only if transformer protection is required | Transformer capacity and maximum loading ratio | 2500 kVA, 90% | Prevents transformer overload | Skip if capacity protection is not requested.
Transformer Capacity | Conditional | Transformer rated capacity | 2500 kVA | Used for capacity protection threshold | Required only if capacity protection is selected.
Maximum Loading Ratio | Conditional | Allowed transformer loading percentage | 90% | Defines protection threshold | Default can be 90% unless customer specifies otherwise.
Power Limitation Mode | Optional - Complete only if selected | Confirm if BESS output power must be limited | Yes - limit per cabinet to 100 kW | Used for breaker/permit/utility limitations | Skip if no power limitation is needed.
Main Circuit Breaker Rating | Conditional | Main breaker rating in A | 3150 A | Ensures power limit matches electrical protection | Required only if power limitation is selected.
Breaker Rating per Unit | Conditional | Breaker rating per BESS unit/cabinet | 315 A | Used for per-cabinet limit | Required only if power limitation is selected.
Power Limit per Cabinet | Conditional | Maximum allowed output power per cabinet | 125 kW / 100 kW | Used for EMS/PCS power limit setting | Required only if power limitation is selected.
Topology Diagram / SLD | Mandatory - Every Project | Latest electrical single-line diagram showing grid, transformer, BESS, PV, meters, breakers | Attach PDF/DWG | Essential for safe commissioning and correct configuration | Must be provided before commissioning.
Communication Topology | Mandatory for Multi-Unit / EMS Projects | Drawing showing EMS, PCS, BMS, meters, PV inverter, router/switch, SCADA | Attach communication diagram | Avoids communication delays on site | Mandatory if EMS1000, multiple units, PV integration, or third-party SCADA is involved.
Internet / Remote Access | Mandatory for Remote Support | Confirm internet, router, DHCP/static IP, VPN restrictions | DHCP available, router installed | Remote commissioning and troubleshooting | Must be completed before remote support.
Emergency Stop / EPO | Mandatory Safety Check / Advanced Details Conditional | Confirm EPO installed and wiring type if applicable | External EPO loop | Safety and PCS control | Basic EPO status required; detailed EPO loop only needed for multi-PCS/advanced backup projects.

## Applicability Summary
Function / Section | Applicability | Customer Action | Note
Project Information | Mandatory - Every Project | Complete all fields | Required before scheduling commissioning
Grid Connection / Delivery Quantity | Mandatory - Every Project | Complete all fields | Required for system configuration
Parallel Operation | Mandatory - Every Project | Select Yes/No | If Yes, EMS1000 / communication coordination required
Peak Shaving & Load Shifting | Standard / If selected | Provide schedule and tariff logic | Typical grid-connected application
PV-ESS Coordination | Optional | Complete only if PV integration is required | Skip if BESS operates independently
Anti-Backflow / Export Limitation | Optional | Complete only if export limitation is required | Meter and CT details required
Demand Control | Optional | Complete only if max demand control is required | Meter and demand limit required
Capacity Protection | Optional | Complete only if transformer protection is required | Transformer capacity required
Power Limitation Mode | Optional | Complete only if output limitation is required | Breaker and per-cabinet power limit required
Black Start | Advanced Optional - Latest Version / Special Project Only | Skip unless explicitly required and confirmed | Not applicable for standard current grid-connected commissioning
Off-Grid System | Advanced Optional - Latest Version / Special Project Only |  | Not applicable for standard current grid-connected commissioning
Topology Diagram / SLD | Mandatory - Every Project | Attach latest SLD | Required before commissioning
Communication Topology | Mandatory for EMS / Multi-Unit / Integration | Attach communication diagram | Avoids on-site communication issues
Network / Remote Access | Mandatory for remote support | Provide router/internet/IP/VPN info | Required for remote commissioning support

## Customer Instructions
Category | Instruction for Customer | Required?
General | If a section is not applicable to your project, write 'N/A' instead of leaving it unclear. | Yes
Standard Projects | For standard grid-connected peak-shaving or load-shifting projects, Black Start and Off-Grid sections can be skipped. | Yes
PV Integration | Complete PV-ESS Coordination only if the battery system must communicate/control PV inverters. | Conditional
Export Limitation | Complete Anti-Backflow / Export Limitation only if the system must prevent exporting power to the grid. | Conditional
Demand Control | Complete Demand Control only if the system must limit maximum import/demand at the grid connection point. | Conditional
Meter | For any meter-based function, provide meter model, meter installation point, CT ratio, Modbus address if available, and communication method. | Conditional
Black Start | Black Start is an advanced optional function and is applicable only for projects requiring backup/microgrid operation and where the latest compatible solution is confirmed. It is not required for standard grid-connected commissioning. | Optional / Advanced
Off-Grid | Off-Grid System is an advanced optional function and is applicable only for projects requiring islanded operation. It is not required for standard grid-connected commissioning. | Optional / Advanced
Black Start / Off-Grid | If Black Start or Off-Grid is selected, provide total critical load power, inrush load details, backup source, switching time requirement, and EMS1000 availability. | Conditional
Power Limitation | Complete Power Limitation Mode only if the customer, grid operator, permit, or breaker rating requires output limitation. | Conditional
Capacity Protection | Complete Capacity Protection only if transformer overload protection is required. | Conditional
Topology | Attach the latest SLD/topology diagram. This is required for every project. | Yes
Communication | For multi-unit or EMS projects, attach communication topology showing EMS, PCS, BMS, meters, router/switch, PV inverter, and third-party systems. | Conditional
Network | Confirm internet/router availability, DHCP/static IP, VPN/firewall restrictions, and whether remote access is allowed. | Yes
Site Readiness | Commissioning can be delayed if power wiring, communication wiring, meter installation, internet, or required diagrams are incomplete. | Yes
EMS Hardware | EMS1000 required to achieve advanced functions of the JA Planet. To install onsite, there needs to be a 24V power source, and a suitable location to install close to the cabinets | Yes
Energy Meters | Only certain meters are compliant with the unit (See attached below). As the unit is RS485, the corresponding meter details need to be shared with the installation team ahead of delivery